Copyright 2012 by The American Institute of Architects (AIA)

Exclusively published and distributed by Architectural Computer Services, Inc. (ARCOM) for the AIA

This Product MasterSpec Section is licensed by ARCOM to Victaulic Company ("Licensee").

This Product MasterSpec Section modifies the original MasterSpec text, and does not include the full content of the original MasterSpec Section.

Revisions made to the original MasterSpec text are made solely by the Licensee and are not endorsed by, or representative of the opinions of, ARCOM or The American Institute of Architects (AIA).  Neither AIA nor ARCOM are liable in any way for such revisions or for the use of this Product MasterSpec Section by any end user.  A qualified design professional should review and edit the document to suit project requirements.

For more information, contact Victaulic Company, 4901 Kesslerville Road, Easton, PA 18042;  Phone: (610) 559-3300; Fax: (610) 250-8817; Website: www.victaulic.com; Email: picvic@victaulic.com.

For information about MasterSpec contact ARCOM at (800) 424-5080 or visit www.MasterSpec.com.

SECTION 211200 - FIRE-SUPPRESSION STANDPIPES

Revise this Section by deleting and inserting text to meet Project-specific requirements.

This Section uses the term "Architect." Change this term to match that used to identify the design professional as defined in the General and Supplementary Conditions.

Verify that Section titles referenced in this Section are correct for this Project's Specifications; Section titles may have changed.

GENERAL

RELATED DOCUMENTS

Retain or delete this article in all Sections of Project Manual.

Drawings and general provisions of the Contract, including General and Supplementary Conditions and Division 01 Specification Sections, apply to this Section.

SUMMARY

Section Includes:

Pipes, fittings, and specialties.

Fire-protection specialty valves.

Hose connections.

Alarm devices.

Manual control stations.

Control panels.

Pressure gages.

Related Requirements:

Retain subparagraphs below that contain requirements Contractor might expect to find in this Section but are specified in other Sections.

Section 210523 "General-Duty Valves for Water-Based Fire-Suppression Piping."

Section 211119 "Fire-Department Connections" for exposed wall-mounted and yard fire hydrants.

Section 211213 "Fire-Suppression Hoses and Nozzles" for rack-type hose stations, reel-type hose stations, and monitors.

Section 211313 "Wet-Pipe Sprinkler Systems" for wet-pipe sprinkler piping.

Section 211316 "Dry-Pipe Sprinkler Systems" for dry-pipe sprinkler piping.

[Section 283111 "Digital, Addressable Fire-Alarm System"] [Section 283112 "Zoned (DC Loop) Fire-Alarm System"] for connections to alarm devices.

DEFINITIONS

Retain terms that remain after this Section has been edited for a project.

Some fire-protection products for high-pressure sprinkler piping are only rated for 250 psig (1725 kPa). If 300-psig (2070-kPa) piping is required, verify product pressure ratings.

High-Pressure Standpipe Piping: Fire-suppression standpipe piping designed to operate at working pressure higher than standard 175 psig (1200 kPa), but not higher than [250 psig (1725 kPa)] [300 psig (2070 kPa)].

Standard-Pressure Standpipe Piping: Fire-suppression standpipe piping designed to operate at working pressure 175 psig (1200 kPa) maximum.

ACTION SUBMITTALS

Product Data: For each type of product.[ Include rated capacities, operating characteristics, electrical characteristics, and furnished specialties and accessories.]

Grooved joint couplings and fittings may be shown on drawings and product submittals, and shall be specifically identified by manufacturer's style and series designation.

Shop Drawings: For fire-suppression standpipes.

Include plans, elevations, sections, and attachment details.

Retain subparagraph below if equipment includes wiring.

Include diagrams for power, signal, and control wiring.

Retain "Delegated-Design Submittal" Paragraph below if design services have been delegated to Contractor.

Delegated-Design Submittal: For standpipe systems indicated to comply with performance requirements and design criteria, including analysis data signed and sealed by the qualified professional engineer responsible for their preparation.

INFORMATIONAL SUBMITTALS

Retain "Coordination Drawings" Paragraph below for situations where limited space necessitates maximum utilization for efficient installation of different components or if coordination is required for installation of products and materials by separate installers. Coordinate paragraph with other Sections specifying products listed below. Preparation of coordination drawings requires the participation of each trade involved in installations within the limited space.

Coordination Drawings: Fire-suppression standpipes, drawn to scale, on which the following items are shown and coordinated with each other, using input from installers of the items involved:

Domestic water piping.

Compressed-air piping.

HVAC hydronic piping.

Nitrogen piping.

<Insert item>.

Coordinate "Qualification Data" Paragraph below with qualification requirements in Section 014000 "Quality Requirements" and as may be supplemented in "Quality Assurance" Article.

Qualification Data: For Installer[ and professional engineer].

Retain "Approved Standpipe Drawings" Paragraph below if design by Contractor is specified in "Performance Requirements" Article.

Approved Standpipe Drawings: Working plans, prepared according to NFPA 14, that have been approved by authorities having jurisdiction, including hydraulic calculations if applicable.

Retain "Welding certificates" Paragraph below if retaining "Welding Qualifications" Paragraph in "Quality Assurance" Article.

Welding certificates.

Retain first paragraph below if report is specified in "Preparation" Article.

Fire-hydrant flow test report.

Field Test Reports and Certificates: Indicate and interpret test results for compliance with performance requirements and as described in NFPA 14. Include "Contractor's Material and Test Certificate for Aboveground Piping" and "Contractor's Material and Test Certificate for Underground Piping."

Field quality-control reports.

CLOSEOUT SUBMITTALS

Operation and Maintenance Data: For fire-suppression standpipes specialties to include in emergency, operation, and maintenance manuals.

QUALITY ASSURANCE

Retain "Installer Qualifications" Paragraph below if Contractor is required to assume responsibility for design of fire-suppression standpipes.

Installer Qualifications:

Retain subparagraph below if Contractor is required to assume responsibility for engineering.

Installer's responsibilities include designing, fabricating, and installing fire-suppression standpipes and providing professional engineering services needed to assume engineering responsibility. Base calculations on results of fire-hydrant flow test.

Retain subparagraph below if Contractor is required to engage a qualified professional engineer.

Engineering Responsibility: Preparation of working plans, calculations, and field test reports by a qualified professional engineer.

Retain "Welding Qualifications" Paragraph below if shop or field welding is required. If retaining, also retain "Welding certificates" Paragraph in "Informational Submittals" Article.

Welding Qualifications: Qualify procedures and operators according to ASME Boiler and Pressure Vessel Code.

Electrical Components, Devices, and Accessories: Listed and labeled as defined in NFPA 70, by a qualified testing agency, and marked for intended location and application.

NFPA Standards: Fire-suppression standpipe equipment, specialties, accessories, installation, and testing shall comply with NFPA 14.

PROJECT CONDITIONS

Retain this article if interruption of existing water-based, fire-suppression standpipe service is required.

Interruption of Existing Fire-Suppression Standpipe Service: Do not interrupt fire-suppression standpipe service to facilities occupied by Owner or others unless permitted under the following conditions and then only after arranging to provide temporary fire-suppression standpipe service according to requirements indicated:

Notify [Architect] [Construction Manager] [Owner] no fewer than [two] <Insert number> days in advance of proposed interruption of fire-suppression standpipe service.

Do not proceed with interruption of fire-suppression standpipe service without [Architect's] [Construction Manager's] [Owner's] written permission.

PRODUCTS

See Editing Instruction No. 1 in the Evaluations for cautions about named manufacturers and products. For an explanation of options and Contractor's product selection procedures, see Section 016000 "Product Requirements."

SYSTEM DESCRIPTIONS

Retain one or more of 11 paragraphs in this article. If using more than one standpipe or sprinkler system, identify each system on Drawings. Delete descriptions of systems not included in this Section.

Automatic Wet-Type, Class I Standpipe System: Includes NPS 2-1/2 (DN 65) hose connections. Has open water-supply valve with pressure maintained and is capable of supplying water demand.

Automatic Wet-Type, Class II Standpipe System: Includes NPS 1-1/2 (DN 40) hose stations. Has open water-supply valve with pressure maintained and is capable of supplying water demand.

Automatic Wet-Type, Class III Standpipe System: Includes NPS 1-1/2 (DN 40) hose stations and NPS 2-1/2 (DN 65) hose connections. Has open water-supply valve with pressure maintained and is capable of supplying water demand.

Automatic Dry-Type, Class I Standpipe System: Includes NPS 2-1/2 (DN 65) hose connections. Has open water-supply valve and dry-pipe valve with standpipes containing compressed air or nitrogen. Opening fire-hose valve releases compressed air and permits water pressure to open dry-pipe valve. Water then flows into standpipes.

Automatic Dry-Type, Class II Standpipe System: Includes NPS 1-1/2 (DN 40) hose stations. Has open water-supply valve and dry-pipe valve with standpipes containing compressed air or nitrogen. Opening fire-hose valve releases compressed air and permits water pressure to open dry-pipe valve. Water then flows into standpipes.

Automatic Dry-Type, Class III Standpipe System: Includes NPS 1-1/2 (DN 40) hose stations and NPS 2-1/2 (DN 65) hose connections. Has open water-supply valve and dry-pipe valve with standpipes containing compressed air or nitrogen. Opening fire-hose valve releases compressed air and permits water pressure to open dry-pipe valve. Water then flows into standpipes.

Semiautomatic Dry-Type, Class I Standpipe System: Includes NPS 2-1/2 (DN 65) hose connections. Has open water-supply valve and deluge valve with standpipes containing air. Actuation of detection device permits water pressure to open deluge valve. Water then flows into standpipes.

Semiautomatic Dry-Type, Class II Standpipe System: Includes NPS 1-1/2 (DN 40) hose stations. Has open water-supply valve and deluge valve with standpipes containing air. Actuation of detection device permits water pressure to open deluge valve. Water then flows into standpipes.

Semiautomatic Dry-Type, Class III Standpipe System: Includes NPS 1-1/2 (DN 40) hose stations and NPS 2-1/2 (DN 65) hose connections. Has open water-supply valve and deluge valve with standpipes containing air. Actuation of detection device permits water pressure to open deluge valve. Water then flows into standpipes.

Manual Wet-Type, Class I Standpipe System: Includes NPS 2-1/2 (DN 65) hose connections. Has small water supply to maintain water in standpipes. Piping is wet, but water must be pumped into standpipes to satisfy demand.

Manual Dry-Type, Class I Standpipe System: Includes NPS 2-1/2 (DN 65) hose connections. Does not have permanent water supply. Piping is dry. Water must be pumped into standpipes to satisfy demand.

PERFORMANCE REQUIREMENTS

Standard-Pressure, Fire-Suppression Standpipe System Component: Listed for 175-psig (1200-kPa) minimum working pressure.

High-Pressure, Fire-Suppression Standpipe System Component: Listed for [250-psig (1725-kPa) minimum] [300-psig (2070-kPa)] [350-psig (2415-kPa)] working pressure.

Retain "Delegated Design" Paragraph below if Contractor is required to assume responsibility for design.

Delegated Design: Design fire-suppression standpipes, including comprehensive engineering analysis by a qualified professional engineer, using performance requirements and design criteria indicated.

Retain data in subparagraph below if known and if Owner wants to furnish test data to Contractor.

Available fire-hydrant flow test records indicate the following conditions:

Date: <Insert test date>.

Time: <Insert time> [a.m.] [p.m.]

Performed by: <Insert operator's name> of <Insert firm>.

Location of Residual Fire Hydrant R: <Insert location>.

Location of Flow Fire Hydrant F: <Insert location>.

Static Pressure at Residual Fire Hydrant R: <Insert psig (kPa)>.

Measured Flow at Flow Fire Hydrant F: <Insert gpm (L/s)>.

Residual Pressure at Residual Fire Hydrant R: <Insert psig (kPa)>.

Retain both paragraphs below if system design has not been approved by authorities having jurisdiction.

Fire-suppression standpipe design shall be approved by authorities having jurisdiction.

Minimum residual pressure at each hose-connection outlet is as follows:

NPS 1-1/2 (DN 40) Hose Connections: [65 psig (450 kPa)] <Insert value>.

NPS 2-1/2 (DN 65) Hose Connections: [100 psig (690 kPa)] <Insert value>.

Seismic Performance: Fire-suppression standpipes shall withstand the effects of earthquake motions determined according to NFPA 13 and [ASCE/SEI 7] <Insert requirement>.

PIPING MATERIALS

See "Writing Guide" Article in the Evaluations for a discussion on this Section's organization and the most efficient way to revise this Section. See "Piping Materials and Standards" Article in the Evaluations for a discussion on availability of piping materials covered by referenced standards in corresponding pipe sizes.

Comply with requirements in "Piping Schedule" Article for applications of pipe, tube, and fitting materials and for joining methods for specific services, service locations, and pipe sizes.

BLACK STEEL PIPE AND ASSOCIATED FITTINGS

Steel pipes in this article are arranged in order of decreasing wall thickness.

All of the steel piping in this article is suitable for 175-psig (1200-kPa) minimum working pressure.

Retain one of three "Schedule 40" paragraphs below for use with flanged, cut- or roll-grooved, plain-end-pipe, threaded, and welded joints.

Schedule 40: ASTM A 53/A 53M, Type E, Grade B; with factory- or field-formed ends to accommodate joining method.

Schedule 40: ASTM A 135/A 135M, Grade A; with factory- or field-formed ends to accommodate joining method.

Schedule 40: ASTM A 795/A 795M, Type E, Grade A; with factory- or field-formed ends to accommodate joining method.

Retain one of three "Schedule 30" paragraphs below for use with flanged, roll-grooved, plain-end-pipe, threaded, and welded joints. Pipe is available in NPS 1/2 to NPS 10 (DN 15 to DN 250).

Schedule 30: ASTM A 53/A 53M, Type E, Grade B; with factory- or field-formed ends to accommodate joining method.

Schedule 30: ASTM A 135/A 135M, Grade A; with factory- or field-formed ends to accommodate joining method.

Schedule 30: ASTM A 795/A 795M, Type E, Grade A; with factory- or field-formed ends to accommodate joining method.

Retain one of three "Thinwall" paragraphs below for use with flanged, roll-grooved, plain-end-pipe, threaded, and welded joints. Pipe is available in NPS 1/2 to NPS 10 (DN 15 to DN 250).

Thinwall: ASTM A 53/A 53M, Type E; with wall thickness less than Schedule 30 and equal to or greater than Schedule 10; and with factory- or field-formed ends to accommodate joining method.

Thinwall: ASTM A 135/A 135M, Grade A; with wall thickness less than Schedule 30 and equal to or greater than Schedule 10; and with factory- or field-formed ends to accommodate joining method.

Thinwall: ASTM A 795/A 795M, Type E, Grade A; with wall thickness less than Schedule 30 and equal to or greater than Schedule 10; and with factory- or field-formed ends to accommodate joining method.

Pipe in "Schedule 10" Paragraph below is intended for use with flanged, roll-grooved, plain-end-pipe, and welded joints. Pipe is available in NPS 1/2 to NPS 10 (DN 15 to DN 250).

Schedule 10: ASTM A 135/A 135M or ASTM A 795/A 795M, Schedule 10 in NPS 5 (DN 125) and smaller; and NFPA 13-specified wall thickness in NPS 6 to NPS 10 (DN 150 to DN 250), plain end.

Caution: Some manufacturers' literature lists lightwall pipe as being threadable. This Section follows the terminology in the "Steel Pipe Schedule" in FM Global's "Approval Guide," which lists thinwall pipe for threading and prohibits threading of hybrid, lightwall pipe. Lightwall pipe may also be referred to as flow pipe or Schedule 7 pipe.

Pipe in "Lightwall" Paragraph below is intended for use with flanged, roll-grooved, plain-end-pipe, and welded joints. Pipe is available in NPS 1/2 to NPS 10 (DN 15 to DN 250).

Lightwall: ASTM A 135/A 135M, [Grade A] <Insert grade>; ASTM A 795/A 795M, [Type E] <Insert type>, [Grade A] <Insert grade>, with wall thickness less than Schedule 10 and greater than Schedule 5.

Couplings in "Uncoated, Steel Couplings" Paragraph below are available in NPS 1/8 to NPS 20 (DN 6 to DN 500).

Uncoated, Steel Couplings: ASTM A 865/A 865M, threaded.

Fittings in "Uncoated, Gray-Iron Threaded Fittings" Paragraph below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

Uncoated, Gray-Iron Threaded Fittings: ASME B16.4, Class 125, standard pattern.

Unions in "Malleable- or Ductile-Iron Unions" Paragraph below are available in NPS 1/4 to NPS 3 (DN 8 to DN 80), but NPFA limits them to NPS 2 (DN 50) and smaller.

Malleable- or Ductile-Iron Unions: UL 860.

Flanges in "Cast-Iron Flanges" Paragraph below are available in NPS 1 to NPS 96 (DN 25 to DN 2400).

Cast-Iron Flanges: ASME B16.1, Class 125.

Flanges and fittings in "Steel Flanges and Flanged Fittings" Paragraph below are available in NPS 1/2 to NPS 24 (DN 15 to DN 600).

Steel Flanges and Flanged Fittings: ASME B16.5, Class 150.

Fittings in "Steel Welding Fittings" Paragraph below are available in NPS 1/2 to NPS 48 (DN 15 to DN 1200).

Steel Welding Fittings: ASTM A 234/A 234M and ASME B16.9.

Grooved-Joint, Steel-Pipe Appurtenances:

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; <Insert product name or designation> of comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Pressure Rating: [175 psig (1200 kPa)] [250 psig (1725 kPa)] [300 psig (2070 kPa)] minimum.

[Galvanized] [and] [Uncoated], Grooved-End Fittings for Steel Piping: ASTM A 536, ductile-iron casting; short pattern, with flow equal to standard pattern, with dimensions matching steel pipe.

AWWA C606 and UL 213 cover couplings in "Grooved-End-Pipe Couplings for Steel Piping" Subparagraph below in NPS 3/4 to at least NPS 12 (DN 20 to at least DN 300).

Grooved-End-Pipe Couplings for Steel Piping: AWWA C606 and UL 213, rigid pattern, unless otherwise indicated, for steel-pipe dimensions. Include ferrous housing sections, EPDM-rubber gasket, and ASTM A 449 electroplated steel bolts and nuts.

Retain one or both of two "Rigid Type Coupling" subparagraphs below.

Rigid Type Couplings:  Housings cast with offsetting, angle-pattern bolt pads to provide joint rigidity and support and hanging in accordance with NFPA-13.  Couplings shall be fully installed at visual pad-to-pad offset contact.  Tongue-and-recess type couplings, or any coupling that requires exact gapping of bolt pads at required torque ratings, are not permitted.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; Style 009N and Style 107H, Installation-Ready, or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Installation:  Suitable for direct stab installation without field disassembly.

Rigid Type Couplings:  Housings cast with offsetting, angle-pattern bolt pads to provide joint rigidity and support and hanging in accordance with NFPA-13.  Couplings shall be fully installed at visual pad-to-pad offset contact.  Tongue-and-recess type couplings, or any coupling that requires exact gapping of bolt pads at required torque ratings, are not permitted.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; Victaulic FireLock Style 005 and Zero-Flex Style 07, or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Retain one or both of two "Flexible Type" subparagraphs below.

Flexible Type:  For use in locations where vibration attenuation and stress relief are required.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; Installation-Ready Style 177, or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Installation:  Suitable for direct stab installation without field disassembly.

Flexible Type:  For use in locations where vibration attenuation and stress relief are required.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; Style 75 and Style 77 or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Retain one of two following "Flange Adapter" subparagraphs.

Flange Adapter:  For direct connection to ANSI Class 125 or 150 flanged connections.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; Style 741 and Style 744 or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Flange Adapter:  For ANSI Class 300 connections.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; Style 743 or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Fittings in "Stainless Steel Pressure-Seal Fittings" paragraph below are available in NPS 3/4 to NPS 2 (DN 20 to DN 50).

Stainless Steel Pressure-Seal Fittings:  FM-approved, 500-psig (3450-kPa) maximum pressure rating with stainless steel housing, elastomer O-rings, and pipe stop; for use with fitting manufacturer's pressure-seal tool Series PFT-510.

Pipe:  Schedule 10S, type 304/304L, conforming to ASTM A 312.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; "Vic-Press" or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

GALVANIZED-STEEL PIPE AND ASSOCIATED FITTINGS

Steel pipes in this article are arranged in order of decreasing wall thickness.

All of the steel piping in this article is suitable for 175-psig (1200-kPa) minimum working pressure.

Retain one of three "Schedule 40" paragraphs below for use with flanged, cut- or roll-grooved, plain-end-pipe, threaded, and welded joints. Pipe is available in NPS 1/8 to NPS 26 (DN 6 to DN 650).

Schedule 40: ASTM A 53/A 53M, Type E, Grade B; with factory- or field-formed ends to accommodate joining method.

Schedule 40: ASTM A 135/A 135M, Grade A; with factory- or field-formed ends to accommodate joining method.

Schedule 40: ASTM A 795/A 795M, Type E, Grade A; with factory- or field-formed ends to accommodate joining method.

Nipples in "Galvanized-Steel Pipe Nipples" Paragraph below are available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

Galvanized-Steel Pipe Nipples: ASTM A 733, made of ASTM A 53/A 53M or ASTM A 106/A 106M, Standard Weight, seamless steel pipe with threaded ends.

Fittings in "Galvanized, Gray-Iron Threaded Fittings" Paragraph below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

Galvanized, Gray-Iron Threaded Fittings: ASME B16.4, Class 125, standard pattern.

Unions in "Malleable-Iron Unions" Paragraph below are available in NPS 1/8 to NPS 4 (DN 6 to DN 100).

Malleable-Iron Unions:

ASME B16.39, Class 150.

Hexagonal-stock body.

Ball-and-socket, metal-to-metal, bronze seating surface.

Threaded ends.

Flanges in "Flanges" Paragraph below are available in NPS 1 to NPS 96 (DN 25 to DN 2400).

Flanges: ASME B16.1, Class 125, cast iron.

Appurtenances for Grooved-End, Galvanized-Steel Pipe:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide Victaulic Company; <Insert product name or designation> comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Fittings for Grooved-End, Galvanized-Steel Pipe: Galvanized, ASTM A 536, ductile-iron casting; short pattern, with flow equal to standard pattern, and with dimensions matching steel pipe.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; FireLock or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

In sizes where short pattern fittings are not available, Victaulic standard fittings may be used.

In "Fittings for Grooved-End, Galvanized-Steel Pipe" Subparagraph below, AWWA C606 covers couplings in NPS 3/4 to NPS 24 (DN 20 to DN 600).

Fittings for Grooved-End, Galvanized-Steel Pipe:

AWWA C606 for steel-pipe dimensions.

Ferrous housing sections.

EPDM-rubber gaskets suitable for hot and cold water.

Bolts and nuts.

Retain one or both "Rigid Type Couplings" subparagraphs below.

Rigid Type Couplings:  Housings cast with offsetting, angle-pattern bolt pads to provide joint rigidity and support and hanging in accordance with NFPA-13.  Couplings shall be fully installed at visual pad-to-pad offset contact.  Tongue-and-recess type couplings, or any coupling that requires exact gapping of bolt pads at required torque ratings, are not permitted.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; Style 009N and Style 107H, Installation-Ready, or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Installation:  Suitable for direct stab installation without field assembly.

Rigid Type Couplings:  Housings cast with offsetting, angle-pattern bolt pads to provide joint rigidity and support and hanging in accordance with NFPA-13.  Couplings shall be fully installed at visual pad-to-pad offset contact.  Tongue-and-recess type couplings, or any coupling that requires exact gapping of bolt pads at required torque ratings, are not permitted.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; FireLock Style 005 and Zero-Flex Style 07, or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Retain one or both of two "Flexible type" subparagraphs below.

Flexible Type:  For use in locations where vibration attenuation and stress relief are required.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; Installation-Ready Style 177 or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Installation:  Suitable for direct stab installation without field assembly.

Flexible Type:  For use in locations where vibration attenuation and stress relief are required.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; Style 75 and Style 77 or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

COPPER TUBE AND ASSOCIATED FITTINGS

All of the copper tubing in this article is suitable for 175-psig (1200-kPa) minimum working pressure.

Tube in "Hard Copper Tube" Paragraph below is available in NPS 1/8 to NPS 12 (DN 6 to DN 300).

Hard Copper Tube: [ASTM B 88, Type L (ASTM B 88M, Type B)] [and] [ASTM B 88, Type M (ASTM B 88M, Type C)] water tube, drawn temper.

Fittings in "Cast-Copper, Solder-Joint Fittings" Paragraph below are available in NPS 1/4 to NPS 12 (DN 8 to DN 300).

Cast-Copper, Solder-Joint Fittings: ASME B16.18, pressure fittings.

Fittings in "Wrought-Copper, Solder-Joint Fittings" Paragraph below are available in NPS 1/4 to NPS 8 (DN 8 to DN 200).

Wrought-Copper, Solder-Joint Fittings: ASME B16.22, pressure fittings.

Flanges in "Bronze Flanges" Paragraph below are available in NPS 1/2 to NPS 12 (DN 15 to DN 300).

Bronze Flanges: ASME B16.24, Class 150, with solder-joint ends.

Unions in "Copper Unions" Paragraph below are available in NPS 1/4 to NPS 4 (DN 8 to DN 100), but NFPA limits them to NPS 2 (DN 50) and smaller.

Copper Unions: MSS SP-123, cast-copper-alloy, hexagonal-stock body, with ball-and-socket, metal-to-metal seating surfaces, and solder-joint or threaded ends.

Grooved-Joint, Copper-Tube Appurtenances:

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; <Insert product name or designation> or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Grooved-End, Copper Fittings: ASME B 16.22 wrought copper and ASTM B 75 (ASTM B 75M), copper tube or ASME B16.18 and ASTM B 584, bronze castings.

In "Grooved-End-Tube Couplings" Subparagraph below, AWWA C606 does not cover couplings for grooved-end copper tubing. One manufacturer makes this type of coupling with dimensions for copper tube and fittings. Another manufacturer has a system for expanding the ends of copper tube and fittings so couplings for steel piping may be used.

Grooved-End-Tube Couplings: To fit copper tube dimensions, with design similar to AWWA C606. Include ferrous housing sections, cast with offsetting, angle-pattern, bolt pads, EPDM elastomer gasket suitable for hot and cold water, and electroplated bolts and nuts conforming to ASTM A 449.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; Style 607H, Installation-Ready or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Installation:  Suitable for direct stab installation without field assembly.

PIPING JOINING MATERIALS

Pipe-Flange Gasket Materials: [AWWA C110, rubber, flat face, 1/8 inch (3.2 mm) thick] [or] [ASME B16.21, nonmetallic and asbestos free].

Class 125, Cast-Iron Flanges and Class 150, Bronze Flat-Face Flanges: Full-face gaskets.

Class 250, Cast-Iron Flanges and Class 300, Steel Raised-Face Flanges: Ring-type gaskets.

Metal, Pipe-Flange Bolts and Nuts: ASME B18.2.1, carbon steel unless otherwise indicated.

Grooved Joint lubricant:  Compatible with gasket elastomer and fluid media.  Supplied by coupling manufacturer.

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; Vic-Lube or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Brazing Filler Metals: AWS A5.8/A5.8M, BCuP Series, copper-phosphorus alloys for general-duty brazing unless otherwise indicated.

Welding Filler Metals: Comply with AWS D10.12/D10.12M for welding materials appropriate for wall thickness and chemical analysis of steel pipe being welded.

SPECIALTY VALVES

General Requirements:

Standard: UL's "Fire Protection Equipment Directory" listing or FM Global's "Approval Guide."

Pressure Rating:

Standard-Pressure Piping Specialty Valves: 175 psig (1200 kPa) minimum.

High-Pressure Piping Specialty Valves: [250 psig (1725 kPa) minimum] [300 psig (2070 kPa)].

Body Material: Cast or ductile iron.

Size: Same as connected piping.

End Connections: Flanged or grooved.

Valves in "Alarm Valves" Paragraph below are available in NPS 1-1/2 to NPS 8 (DN 40 to DN 200).

Alarm Valves:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide Victaulic Company; Series 751 or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Standard: UL 193.

Design: For vertical installation.

Internal components shall be replaceable without removing valve from installed position.

Delete option in first subparagraph below if water-supply pressure is constant.

Include trim sets for bypass, drain, electrical sprinkler alarm switch, pressure gages,[ retarding chamber,] and fill-line attachment with strainer.

Retain one of two "Drip Cup Assembly" subparagraphs below. Retain first subparagraph if retarding chamber is required. Retain second if retarding chamber is not required.

Drip Cup Assembly: Pipe drain without valves and separate from main drain piping.

Drip Cup Assembly: Pipe drain with check valve to main drain piping.

Retain "Dry-Pipe Valves" Paragraph below for dry-type standpipes. Valves are available in NPS 1-1/2 to NPS 8 (DN 40 to DN 200).

Dry-Pipe Valves:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide Victaulic Company; Series 768-NXT or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Standard: UL 260.

Required Air Pressure:  13-psig (90-kPa).

Design: Differential-pressure type.

Internal components shall be replaceable without removing valve from installed position.

Valve shall be externally resettable.

Include UL 1486, quick-opening devices, trim sets for air supply, drain, priming level, alarm connections, ball drip valves, pressure gages, priming chamber attachment, and fill-line attachment.

Retain "Air-Pressure Maintenance Device" Subparagraph below if system uses an air-pressure maintenance device. If retaining, delete "Air Compressor" Subparagraph.

Air-Pressure Maintenance Device:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide Victaulic Company; <Insert product name or designation> or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Standard: UL 260.

Type: Automatic device to maintain minimum air pressure in piping.

Include shutoff valves to permit servicing without shutting down sprinkler piping, bypass valve for quick filling, pressure regulator or switch to maintain pressure, strainer, pressure ratings with 14- to 60-psig (95- to 410-kPa) adjustable range, and [175-psig (1200-kPa)] [300-psig (2070-kPa)] outlet pressure.

Retain "Air Compressor" Subparagraph below if system contains an air compressor. If retaining, delete "Air-Pressure Maintenance Device" Subparagraph.

Air Compressor:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Gast Manufacturing Inc.

<Insert engineer approved manufacturer's name>.

Standard: UL's "Fire Protection Equipment Directory" listing.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 210513 "Common Motor Requirements for Fire Suppression Equipment." If different characteristics are required, insert subparagraphs below to suit Project.

Motor Horsepower: Fractional.

Power: 120-V ac, 60 Hz, single phase.

Deluge Valves:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide Victaulic Company; Series 769-NXT or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Standard: UL 260.

Valve:  Externally resettable.

Internal Components:  Replaceable without removing valve from installed position.

Design: Hydraulically operated, differential-pressure type.

Include trim sets for bypass, drain, electrical sprinkler alarm switch, pressure gages, drip cup assembly piped without valves and separate from main drain line, fill-line attachment with strainer, and push-rod chamber supply connection.

Retain "Wet, Pilot-Line Trim Set" Subparagraph below for wet-type standpipes, hydraulic manual control, or solenoid-valve actuation.

Wet, Pilot-Line Trim Set: Include gage to read push-rod chamber pressure, globe valve for manual operation of deluge valve, and connection for actuation device.

Retain "Dry, Pilot-Line Trim Set" Subparagraph below for dry-type standpipes; provide air supply.

Dry, Pilot-Line Trim Set: Include dry, pilot-line actuator; air- and water-pressure gages; low-air-pressure warning switch; air relief valve; and actuation device. Dry, pilot-line actuator includes cast-iron, operated, diaphragm-type valve with resilient facing plate, resilient diaphragm, and replaceable bronze seat. Valve includes threaded water and air inlets and water outlet. Loss of air pressure on dry, pilot-line side allows pilot-line actuator to open and causes deluge valve to open immediately.

Retain "Air-Pressure Maintenance Device" Subparagraph below if system uses air-pressure maintenance devices. If retaining, delete "Air Compressor" Subparagraph.

Air-Pressure Maintenance Device:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide Victaulic Company; <Insert product name or designation> or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Standard: UL 260.

Type: Automatic device to maintain minimum air pressure in piping.

Include shutoff valves to permit servicing without shutting down sprinkler piping, bypass valve for quick filling, pressure regulator, or switch to maintain pressure, strainer, pressure ratings with 14- to 60-psig (95- to 410-kPa) adjustable range, and [175-psig (1200-kPa)] [300-psig (2070-kPa)] outlet pressure.

Retain "Air Compressor" Subparagraph below if system contains an air compressor. If retaining, delete "Air-Pressure Maintenance Device" Subparagraph.

Air Compressor:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Gast Manufacturing Inc.

<Insert engineer approved manufacturer's name>.

Standard: UL's "Fire Protection Equipment Directory" listing.

Motor characteristics such as NEMA designation, temperature rating, service factor, enclosure type, and efficiency are specified in Section 210513 "Common Motor Requirements for Fire Suppression Equipment." If different characteristics are required, insert subparagraphs below to suit Project.

Motor Horsepower: Fractional.

Power: 120-V ac, 60 Hz, single phase.

Valves in "Pressure-Reducing Valves" Paragraph below are used on standpipe risers.

Pressure-Reducing Valves:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

CLA-VAL Automatic Control Valves.

Fire-End & Croker Corporation.

Fire Protection Products, Inc.

Guardian Fire Equipment, Inc.

OCV Control Valves.

Potter Roemer.

Zurn Plumbing Products Group; Wilkins Water Control Products Division.

<Insert manufacturer's name>.

Indicate valve size and inlet and outlet pressures on Drawings for each pressure-reducing valve.

UL 668 hose valve, with integral UL 1468 reducing device.

Pressure Rating: 300 psig (2070 kPa) minimum.

Material: Brass or bronze.

Inlet: Female pipe threads.

Outlet: Threaded with or without adapter having male hose threads.

Pattern: [Angle] [or] [gate].

Finish: [Polished chrome-plated] [Rough brass or bronze] [Rough chrome-plated].

Automatic (Ball Drip) Drain Valves:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Reliable Automatic Sprinkler Co., Inc.

<Insert manufacturer's name>.

Standard: UL 1726.

Pressure Rating: 175 psig (1200 kPa) minimum.

Type: Automatic draining, ball check.

Size: NPS 3/4 (DN 20).

End Connections: Threaded.

HOSE CONNECTIONS

Coordinate cabinets with Section 104413 "Fire Protection Cabinets." Indicate size and design outlet pressure setting on Drawings for each hose connection.

Adjustable-Valve Hose Connections:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Brooks Equipment Co., Inc.

Elkhart Brass Mfg. Company, Inc.

Fire-End & Croker Corporation.

<Insert engineer approved manufacturer's name>.

Standard: UL 668 hose valve, with integral UL 1468 reducing or restricting pressure-control device, for connecting fire hose.

Pressure Rating: 300 psig (2070 kPa) minimum.

Material: Brass or bronze.

Size: NPS 1-1/2 or NPS 2-1/2 (DN 40 or DN 65), as indicated.

Inlet: Female pipe threads.

Outlet: Male hose threads with lugged cap, gasket, and chain. Include hose valve threads according to NFPA 1963 and matching local fire-department threads.

Pattern: [Angle] [or] [gate].

Pressure-Control Device Type: Pressure [reducing] [restricting].

Design Outlet Pressure Setting: <Insert psig (kPa)>.

Finish: [Polished chrome-plated] [Rough brass or bronze] [Rough chrome-plated].

Nonadjustable-Valve Hose Connections:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Retain "Basis-of-Design Product" Subparagraph and list of manufacturers below to identify a specific product or a comparable product from manufacturers listed. Retain option and delete insert note if manufacturer's name and model number are indicated on Drawings.

Basis-of-Design Product: Subject to compliance with requirements, provide [product indicated on Drawings] <Insert manufacturer's name; product name or designation> or comparable product by one of the following:

Brooks Equipment Co., Inc.

NIBCO INC.

Viking Corporation.

<Insert engineer approved manufacturer's name>.

Standard: UL 668 hose valve for connecting fire hose.

Pressure Rating: 300 psig (2070 kPa) minimum.

Material: Brass or bronze.

Size: NPS 1-1/2 or NPS 2-1/2 (DN 40 or DN 65), as indicated.

Inlet: Female pipe threads.

Outlet: Male hose threads with lugged cap, gasket, and chain. Include hose valve threads according to NFPA 1963 and matching local fire-department threads.

Pattern: [Angle] [or] [gate].

Finish: [Polished chrome-plated] [Rough brass or bronze] [Rough chrome-plated].

ALARM DEVICES

Alarm-device types shall match piping and equipment connections.

Retain remaining paragraphs if devices are specified in this Section, or delete if devices are specified in Section 283111 "Digital, Addressable Fire-Alarm System" and Section 283112 "Zoned (DC Loop) Fire-Alarm System."

Water-Motor-Operated Alarm:

Basis-of-Design Product:  Subject to compliance with requirements, provide Victaulic Company; <Insert product name or designation> or comparable product by one of the following:

<Insert engineer approved manufacturer's name>.

Standard: UL 753.

Type: Mechanically operated, with pelton wheel.

Alarm Gong: Cast aluminum with red-enamel factory finish.

Size: 10-inch (250-mm) diameter.

Components: Shaft length, bearings, and sleeve to suit wall construction.

Inlet: NPS 3/4 (DN 20).

Outlet: NPS 1 (DN 25) drain connection.

Electrically Operated Alarm Bell:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Fire-Lite Alarms, Inc.; a Honeywell company.

Notifier; a Honeywell company.

Potter Electric Signal Company.

<Insert manufacturer's name>.

Standard: UL 464.

Type: Vibrating, metal alarm bell.

Size: [6-inch (150-mm) minimum] [8-inch (200-mm) minimum] [10-inch (250-mm)] diameter.

Finish: Red-enamel factory finish, suitable for outdoor use.

Water-Flow Indicators:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

System Sensor; a Honeywell company.

Viking Corporation.

Watts Industries (Canada) Inc.

<Insert engineer approved manufacturer's name>.

Standard: UL 346.

Water-Flow Detector: Electrically supervised.

Components: Two single-pole, double-throw circuit switches for isolated alarm and auxiliary contacts, 7 A, 125-V ac and 0.25 A, 24-V dc; complete with factory-set, field-adjustable retard element to prevent false signals and tamperproof cover that sends signal if removed.

Type: Paddle operated.

Pressure Rating: 250 psig (1725 kPa).

Design Installation: Horizontal or vertical.

Pressure Switches:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Potter Electric Signal Company.

System Sensor; a Honeywell company.

Viking Corporation.

<Insert engineer approved manufacturer's name>.

Standard: UL 346.

Type: Electrically supervised water-flow switch with retard feature.

Components: Single-pole, double-throw switch with normally closed contacts.

Design Operation: Rising pressure signals water flow.

Valve Supervisory Switches:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Fire-Lite Alarms, Inc.; a Honeywell company.

Potter Electric Signal Company.

System Sensor; a Honeywell company.

<Insert engineer approved manufacturer's name>.

Standard: UL 346.

Type: Electrically supervised.

Components: Single-pole, double-throw switch with normally closed contacts.

Design: Signals that controlled valve is in other than fully open position.

Indicator-Post Supervisory Switches:

Retain "Manufacturers" Subparagraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

Potter Electric Signal Company.

System Sensor; a Honeywell company.

<Insert manufacturer's name>.

Standard: UL 346.

Type: Electrically supervised.

Components: Single-pole, double-throw switch with normally closed contacts.

Design: Signals that controlled indicator-post valve is in other than fully open position.

MANUAL CONTROL STATIONS

Retain this article for dry-type standpipe system piping; delete if using "Control Panels" Article or if control stations are specified in Section 283111 "Digital, Addressable Fire-Alarm System" and Section 283112 "Zoned (DC Loop) Fire-Alarm System."

Description: UL listed or FM Global approved, hydraulic operation, with union, NPS 1/2 (DN 15) pipe nipple, and bronze ball valve. Include metal enclosure labeled "MANUAL CONTROL STATION" with operating instructions and cover held closed by breakable strut to prevent accidental opening.

CONTROL PANELS

Retain this article for dry-type standpipe system piping; delete if using "Manual Control Stations" Article or if controls are specified in Section 283111 "Digital, Addressable Fire-Alarm System" and Section 283112 "Zoned (DC Loop) Fire-Alarm System."

Description: Single-area, two-area, or single-area cross-zoned control panel as indicated, including NEMA ICS 6, Type 1 enclosure, detector, alarm, and solenoid-valve circuitry for operation of deluge valves. Panels contain power supply; battery charger; standby batteries; field-wiring terminal strip; electrically supervised solenoid valves and polarized fire-alarm bell; lamp test facility; single-pole, double-throw auxiliary alarm contacts; and rectifier.

Panels: UL listed and FM Global approved when used with thermal detectors and Class A detector circuit wiring. Electrical characteristics are 120-V ac, 60 Hz, with 24-V dc rechargeable batteries.

Retain one of two "Manual Control Stations" subparagraphs below.

Manual Control Stations: Electric operation, metal enclosure, labeled "MANUAL CONTROL STATION" with operating instructions and cover held closed by breakable strut to prevent accidental opening.

Manual Control Stations: Hydraulic operation, with union, NPS 1/2 (DN 15) pipe nipple, and bronze ball valve. Include metal enclosure labeled "MANUAL CONTROL STATION" with operating instructions and cover held closed by breakable strut to prevent accidental opening.

PRESSURE GAGES

Retain "Manufacturers" Paragraph and list of manufacturers below to require products from manufacturers listed or a comparable product from other manufacturers.

Manufacturers: Subject to compliance with requirements, [provide products by the following] [provide products by one of the following] [available manufacturers offering products that may be incorporated into the Work include, but are not limited to, the following]:

AMETEK; U.S. Gauge Division.

Ashcroft Inc.

Brecco Corporation.

WIKA Instrument Corporation.

<Insert manufacturer's name>.

Standard: UL 393.

Dial Size: 3-1/2- to 4-1/2-inch (90- to 115-mm) diameter.

Pressure Gage Range: [Zero to 250 psig (Zero to 1725 kPa) minimum] [Zero to 300 psig (Zero to 2070 kPa)].

Water System Piping Gage: Include "WATER" or "AIR/WATER" label on dial face.

Air System Piping Gage: Include[ retard feature and] "AIR" or "AIR/WATER" label on dial face.

EXECUTION

PREPARATION

Retain this article if fire-hydrant flow test is required or if Owner has not provided flow information.

Perform fire-hydrant flow test according to NFPA 14 and NFPA 291. Use results for system design calculations required in "Quality Assurance" Article.

Report test results promptly and in writing.

EXAMINATION

Examine roughing-in for hose connections and stations to verify actual locations of piping connections before installation.

Examine walls and partitions for suitable thickness, fire- and smoke-rated construction, framing for hose-station cabinets, and other conditions where hose connections and stations are to be installed.

Proceed with installation only after unsatisfactory conditions have been corrected.

SERVICE-ENTRANCE PIPING

Retain this article and delete "Water-Supply Connections" Article if connection to building's water-service piping is required.

Connect fire-suppression standpipe piping to water-service piping at service entrance into building. Comply with requirements for exterior piping in Section 211100 "Facility Fire-Suppression Water-Service Piping."

Retain one of two paragraphs below. Backflow preventers are recommended and are usually required by authorities having jurisdiction. Do not specify backflow preventers here if they are specified in Section 211100 "Facility Fire-Suppression Water-Service Piping."

Install shutoff valve,[ backflow preventer,] pressure gage, drain, and other accessories at connection to fire-suppression water-service piping.[ Comply with requirements for backflow preventers in Section 211100 "Facility Fire-Suppression Water-Service Piping."]

Install shutoff valve, check valve, pressure gage, and drain at connection to water service.

WATER-SUPPLY CONNECTIONS

Retain this article and delete "Service-Entrance Piping" Article if connection to building's water-distribution piping is required.

Connect fire-suppression standpipe piping to building's interior water-distribution piping. Comply with requirements for interior piping in Section 221116 "Domestic Water Piping."

Retain one of two paragraphs below. Backflow preventers are recommended and are usually required by authorities having jurisdiction.

Install shutoff valve,[ backflow preventer,] pressure gage, drain, and other accessories at connection to water-distribution piping.[ Comply with requirements for backflow preventers in Section 221119 "Domestic Water Piping Specialties."]

Install shutoff valve, check valve, pressure gage, and drain at connection to water supply.

PIPING INSTALLATION

Locations and Arrangements: Drawing plans, schematics, and diagrams indicate general location and arrangement of piping. Install piping as indicated, as far as practical.

Deviations from approved working plans for piping require written approval from authorities having jurisdiction. File written approval with Architect before deviating from approved working plans.

Piping Standard: Comply with requirements in NFPA 14 for installation of fire-suppression standpipe piping.

Retain first paragraph below if piping is required to withstand seismic design loads.

Install seismic restraints on piping. Comply with requirements in NFPA 13 for seismic-restraint device materials and installation.

Install listed fittings to make changes in direction, branch takeoffs from mains, and reductions in pipe sizes.

Install drain valves on standpipes. Extend drain piping to outside of building.

Install automatic (ball drip) drain valves to drain piping between fire-department connections and check valves. Drain to floor drain or outside building.

Install alarm devices in piping systems.

See Editing Instruction No. 3 in the Evaluations for cautions about pipe hangers.

Install hangers and supports for standpipe system piping according to NFPA 14. Comply with requirements in NFPA 13 for hanger materials.

Install pressure gages on riser or feed main and at top of each standpipe. Include pressure gages with connection not less than NPS 1/4 (DN 8) and with soft-metal seated globe valve, arranged for draining pipe between gage and valve. Install gages to permit removal, and install where they are not subject to freezing.

Drain dry-type standpipe system piping.

Pressurize and check dry-type standpipe system piping and [air-pressure maintenance devices] [air compressors].

Fill wet-type standpipe system piping with water.

Install electric heating cables and pipe insulation on wet-type fire-suppression standpipe piping in areas subject to freezing. Comply with requirements for heating cables in Section 210533 "Heat Tracing for Fire-Suppression Piping" and for piping insulation in Section 210700 "Fire-Suppression Systems Insulation."

Retain one of first two paragraphs below.

Connect compressed-air or nitrogen supply to dry-pipe sprinkler piping.

Connect air compressor to the following piping and wiring:

Pressure gages and controls.

Electrical power system.

Fire-alarm devices, including low-pressure alarm.

Install sleeves for piping penetrations of walls, ceilings, and floors. Comply with requirements for sleeves specified in Section 210517 "Sleeves and Sleeve Seals for Fire-Suppression Piping."

Retain first paragraph below for piping that penetrates an exterior concrete wall or concrete slab.

Install sleeve seals for piping penetrations of concrete walls and slabs. Comply with requirements for sleeve seals specified in Section 210517 "Sleeves and Sleeve Seals for Fire-Suppression Piping."

Install escutcheons for piping penetrations of walls, ceilings, and floors. Comply with requirements for escutcheons specified in Section 210518 "Escutcheons for Fire-Suppression Piping."

JOINT CONSTRUCTION

Install couplings, flanges, flanged fittings, unions, nipples, and transition and special fittings that have finish and pressure ratings same as or higher than system's pressure rating for aboveground applications unless otherwise indicated.

Install unions adjacent to each valve in pipes NPS 2 (DN 50) and smaller.

Install flanges, flange adapters, or couplings for grooved-end piping on valves, apparatus, and equipment having NPS 2-1/2 (DN 65) and larger end connections.

Ream ends of pipes and tubes, and remove burrs. Bevel plain ends of steel pipe.

Remove scale, slag, dirt, and debris from inside and outside of pipes, tubes, and fittings before assembly.

Flanged Joints: Select appropriate gasket material in size, type, and thickness suitable for water service. Join flanges with gasket and bolts according to ASME B31.9.

Threaded Joints: Thread pipe with tapered pipe threads according to ASME B1.20.1. Cut threads full and clean using sharp dies. Ream threaded pipe ends to remove burrs and restore full ID. Join pipe fittings and valves as follows:

Apply appropriate tape or thread compound to external pipe threads.

Damaged Threads: Do not use pipe or pipe fittings with threads that are corroded or damaged.

Steel-Piping, Cut-Grooved Joints: Cut square-edge groove in end of pipe according to AWWA C606. Assemble coupling with housing, gasket, lubricant, and bolts. Join steel pipe and grooved-end fittings according to AWWA C606 for steel-pipe joints.

Assure grooved ends are clean and free from indentations, projections, or roll marks.

Use gaskets molded and produced by coupling manufacturer of an elastomer suitable for intended service.

On-site Training:  For contractor's field personnel in use of grooving tools and installation of product shall be provided by coupling manufacturer's factory-trained representative. (Distributor representative is not considered qualified to conduct the training.)

Job Site Visitation:  Manufacturer's representative shall periodically visit jobsite to ensure best practices in grooved product installation are followed.

Where required, retain the subparagraphs below:

The installing contractor shall be certified by the grooved coupling manufacturer for the installation of their product. A manufacturer’s factory trained representative (direct employee) shall provide on-site certification training for the installing contractor’s field personnel in the use of grooving tools, application of groove, and product installation

A field training program must be designed, developed, administered and evaluated in accordance to the ANSI/IACET Standard for Continuing Education and Training. (IACET-International Association for Continuing Education and Training)

All installation professionals and pipe fitters must be able to provide proof of successful course completion upon request

Steel-Piping, Roll-Grooved Joints: Roll rounded-edge groove in end of pipe according to AWWA C606. Assemble coupling with housing, gasket, lubricant, and bolts. Join steel pipe and grooved-end fittings according to AWWA C606 for steel-pipe grooved joints.

Assure grooved ends are clean and free from indentations, projections, or roll marks.

Use gaskets molded and produced by coupling manufacturer of an elastomer suitable for intended service.

On-site Training:  For contractor's field personnel in use of grooving tools and installation of product shall be provided by coupling manufacturer's factory-trained representative. (Distributor representative is not considered qualified to conduct the training.)

Job Site Visitation:  Manufacturer's representative shall periodically visit jobsite to ensure best practices in grooved product installation are followed.

Where required, retain the subparagraphs below:

The installing contractor shall be certified by the grooved coupling manufacturer for the installation of their product. A manufacturer’s factory trained representative (direct employee) shall provide on-site certification training for the installing contractor’s field personnel in the use of grooving tools, application of groove, and product installation

A field training program must be designed, developed, administered and evaluated in accordance to the ANSI/IACET Standard for Continuing Education and Training. (IACET-International Association for Continuing Education and Training)

All installation professionals and pipe fitters must be able to provide proof of successful course completion upon request

Welded Joints: Construct joints according to AWS D10.12/D10.12M, using qualified processes and welding operators according to "Quality Assurance" Article.

Shop weld pipe joints where welded piping is indicated. Do not use welded joints for galvanized-steel pipe.

Brazed Joints: Join copper tube and fittings according to CDA's "Copper Tube Handbook," "Brazed Joints" Chapter.

Copper-Tubing Grooved Joints: Roll rounded-edge groove in end of tube according to AWWA C606. Assemble coupling with housing, gasket, lubricant, and bolts. Join copper tube and grooved-end fittings according to AWWA C606 for steel-pipe grooved joints.

Dissimilar-Material Piping Joints: Make joints using adapters compatible with materials of both piping systems.

VALVE AND SPECIALTIES INSTALLATION

Install listed fire-protection valves, trim and drain valves, specialty valves and trim, controls, and specialties according to NFPA 14 and authorities having jurisdiction.

Install listed fire-protection shutoff valves supervised-open, located to control sources of water supply except from fire-department connections. Install permanent identification signs indicating portion of system controlled by each valve.

Install check valve in each water-supply connection. Install backflow preventers instead of check valves in potable-water-supply sources.

Specialty Valves:

General Requirements: Install in vertical position for proper direction of flow, in main supply to system.

Alarm Valves: Install bypass check valve and retarding chamber drain-line connection.

[Dry-Pipe] [and] [Deluge] Valves: Install trim sets for air supply, drain, priming level, alarm connections, ball drip valves, pressure gages, priming chamber attachment, and fill-line attachment.

Retain first subparagraph or second and third subparagraphs below.

Install air compressor and compressed-air supply piping.

Air-Pressure Maintenance Device: Install shutoff valves to permit servicing without shutting down sprinkler system; bypass valve for quick system filling; pressure regulator or switch to maintain system pressure; strainer; pressure ratings with [14- to 60-psig (95- to 410-kPa)] <Insert value> adjustable range; and [175-psig (1200-kPa)] <Insert value> maximum inlet pressure.

Install compressed-air supply piping from building's compressed-air piping system.

HOSE-CONNECTION INSTALLATION

Indicate hose-connection locations, sizes, and special devices on Drawings.

Install hose connections adjacent to standpipes.

Install freestanding hose connections for access and minimum passage restriction.

Install NPS 1-1/2 (DN 40) hose-connection valves with flow-restricting device.

Install NPS 2-1/2 (DN 65) hose connections with quick-disconnect NPS 2-1/2 by NPS 1-1/2 (DN 65 by DN 40) reducer adapter and flow-restricting device.

Install wall-mounted-type hose connections in cabinets. Include pipe escutcheons, with finish matching valves, inside cabinet where water-supply piping penetrates cabinet. Install valves at angle required for connection of fire hose. Comply with requirements for cabinets in Section 104413 "Fire Protection Cabinets."

HOSE-STATION INSTALLATION

Indicate hose-station locations, sizes, and special devices on Drawings.

Install freestanding hose stations for access and minimum passage restriction.

Install NPS 1-1/2 (DN 40) hose-station valves with flow-restricting device unless otherwise indicated.

Install NPS 2-1/2 (DN 65) hose connections with quick-disconnect NPS 2-1/2 by NPS 1-1/2 (DN 65 by DN 40) reducer adapter and flow-restricting device unless otherwise indicated.

Install freestanding hose stations with support or bracket attached to standpipe.

Install wall-mounted, rack hose stations in cabinets. Include pipe escutcheons, with finish matching valves, inside cabinet where water-supply piping penetrates cabinet. Install valves at angle required for connection of fire hose. Comply with requirements for cabinets in Section 104413 "Fire Protection Cabinets."

Install hose-reel hose stations on wall with bracket.

FIRE-DEPARTMENT CONNECTION INSTALLATION

Install wall-type fire-department connections.

Install yard-type fire-department connections in concrete slab support. Comply with requirements for concrete in Section 033000 "Cast-in-Place Concrete."

Install [two] [three] <Insert number> protective pipe bollards [around] [on sides of] each fire-department connection. Comply with requirements for bollards in Section 055000 "Metal Fabrications."

Install automatic (ball drip) drain valve at each check valve for fire-department connection.

At the low point near each fire department connection, install a 90-degree elbow with drain connection to allow for system drainage to prevent freezing.  Basis-of-Design:  Victaulic #10-DR.

IDENTIFICATION

Install labeling and pipe markers on equipment and piping according to requirements in NFPA 14.

Identify system components, wiring, cabling, and terminals. Comply with requirements for identification specified in Section 260553 "Identification for Electrical Systems."

FIELD QUALITY CONTROL

Perform tests and inspections.

Retain "Tests and Inspections" Paragraph below to describe tests and inspections to be performed.

Tests and Inspections:

Leak Test: After installation, charge systems and test for leaks. Repair leaks and retest until no leaks exist.

Test and adjust controls and safeties. Replace damaged and malfunctioning controls and equipment.

Flush, test, and inspect standpipe systems according to NFPA 14, "System Acceptance" Chapter.

Energize circuits to electrical equipment and devices.

Start and run air compressors.

Coordinate with fire-alarm tests. Operate as required.

Coordinate with fire-pump tests. Operate as required.

Verify that equipment hose threads are same as local fire-department equipment.

See Section 014000 "Quality Requirements" for retesting and reinspecting requirements and Section 017300 "Execution" for requirements for correcting the Work.

Fire-suppression standpipe system will be considered defective if it does not pass tests and inspections.

Prepare test and inspection reports.

DEMONSTRATION

[Engage a factory-authorized service representative to train] [Train] Owner's maintenance personnel to adjust, operate, and maintain specialty valves.

PIPING SCHEDULE

See Editing Instruction No. 2 in the Evaluations for available materials.

Retain piping applications in this article. Coordinate with materials specified in Part 2.

Piping between Fire-Department Connections and Check Valves: Galvanized, standard-weight steel pipe with [threaded ends; cast-iron threaded fittings; and threaded] [grooved ends; grooved-end fittings; grooved-end-pipe couplings; and grooved] joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

Standard-pressure, wet-type fire-suppression standpipe piping, [NPS 4 (DN 100) and smaller] <Insert pipe size range>, shall be[ one of] the following:

Retain one or more of nine subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

[Schedule 40] [or] [Schedule 30], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [Schedule 30] [or] [thinwall], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [or] [Schedule 30], black-steel pipe with [cut-] [or] [roll-]grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Schedule 40] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

[Thinwall] [Schedule 10,] [or] [lightwall] black-steel pipe with roll-grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Thinwall] [Schedule 10,] [or] [lightwall] black-steel pipe with plain ends; welding fittings; and welded joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with plain ends; [cast-] [or] [wrought-]copper solder-joint fittings; and brazed joints.

[Type L (Type B)] [Type M (Type B)], hard copper tube with roll-grooved ends; copper, grooved-end fittings; grooved-end-tube couplings; and grooved joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

Standard-pressure, wet-type fire-suppression standpipe piping, [NPS 5 to NPS 8 (DN 125 to DN 200)] <Insert pipe size range>, shall be[ one of] the following:

Retain one or more of nine subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

[Schedule 40] [Schedule 30] [or] [thinwall], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [or] [Schedule 30], black-steel pipe with [cut-] [or] [roll-]grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Schedule 40] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

[Thinwall] [Schedule 10,] [or] [lightwall] black-steel pipe with roll-grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Thinwall] [Schedule 10,] [or] [lightwall] black-steel pipe with plain ends; welding fittings; and welded joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with plain ends; [cast-] [or] [wrought-]copper solder-joint fittings; and brazed joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with roll-grooved ends; copper, grooved-end fittings; grooved-end-tube couplings; and grooved joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

Standard-pressure, wet-type fire-suppression standpipe piping, [NPS 10 and NPS 12 (DN 250 and DN 300)] <Insert pipe size range>, shall be[ one of] the following:

Retain one or more of six subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

[Schedule 40] [or] [Schedule 30], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [or] [Schedule 30], black-steel pipe with [cut-] [or] [roll-]grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Schedule 40] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

[Thinwall] [Schedule 10,] [or] [lightwall] black-steel pipe with plain ends; welding fittings; and welded joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

High-pressure, wet-type fire-suppression standpipe piping, [NPS 4 (DN 100) and smaller] <Insert pipe size range>, shall be[ one of] the following:

Retain one or more of six subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

[Schedule 40] [or] [Schedule 30], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [or] [Schedule 30], black-steel pipe with [cut] [cut- or roll] [roll]-grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Schedule 40] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

[Thinwall] [Schedule 10,] [or] [lightwall] black-steel pipe with plain ends; welding fittings; and welded joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

High-pressure, wet-type fire-suppression standpipe piping, [NPS 5 (DN 125) and larger] <Insert pipe size range>, shall be[ one of] the following:

Retain one or more of six subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

[Schedule 40] [or] [Schedule 30], black-steel pipe with threaded ends; uncoated, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [or] [Schedule 30], black-steel pipe with [cut-] [or] [roll-]grooved ends; uncoated, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Schedule 40] [or] [Schedule 30], black-steel pipe with plain ends; steel welding fittings; and welded joints.

[Thinwall] [Schedule 10,] [or] [lightwall] black-steel pipe with plain ends; welding fittings; and welded joints.

Retain " one of" option in first paragraph below to allow Contractor to select piping materials from those retained.

Standard-pressure, dry-type fire-suppression standpipe piping, [NPS 4 (DN 100) and smaller] <Insert pipe size range>, shall be[ one of] the following:

Retain one or more of four subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with plain ends; [cast-] [or] [wrought-]copper solder-joint fittings; and brazed joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with roll-grooved ends; copper, grooved-end fittings; grooved-end-tube couplings; and grooved joints.

Retain " one of" option in paragraph below to allow Contractor to select piping materials from those retained.

Standard-pressure, dry-type fire-suppression standpipe piping, [NPS 5 and NPS 6 (DN 125 and DN 150)] <Insert pipe size range>, shall be[ one of] the following:

Retain one or more of four subparagraphs below. If using more than one type of material and joining method, identify various materials on Drawings and show points of transition from one material to another.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with threaded ends; galvanized, gray-iron threaded fittings; and threaded joints.

[Schedule 40] [or] [Schedule 30], galvanized-steel pipe with cut-grooved ends; galvanized, grooved-end fittings for steel piping; grooved-end-pipe couplings for steel piping; and grooved joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with plain ends; [cast-] [or] [wrought-]copper solder-joint fittings; and brazed joints.

[Type L (Type B)] [Type M (Type C)], hard copper tube with roll-grooved ends; copper, grooved-end fittings; grooved-end-tube couplings; and grooved joints.

END OF SECTION 211200